|  |  |  |
| --- | --- | --- |
| **BOILER SPECIFICATION** | | |
| **Equipment:** BOILERS **Supplier:** HEVAC Ltd. | |
| **General Description of Equipment offered for SPECIFICATION /Approval:**   * BOILER SPECIFICATION | | |
| **Drawing: Dims. as per drawing below.** | **Drawing Ref: N/A** | |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **DOCUMENTATION ISSUED:**   |  |  | | --- | --- | | **SPECIFICATION** | **DEDIETRICH FLOOR WALL HUNG GAS CONDENSING BOILER** | | **TYPE** | INNOVENS PRO | | **REF.** | MCA 160 | | **NOMINAL OUTPUT @ 50/30°C** | 161.5kW | | **Full load central heating efficiency (Hi) (80/60°C) (92/42/EEC)** | 97.5 % | | **Full load central heating efficiency (Hi) (50°C/30°C) (EN15502)** | 103.6% | | **Low load central heating efficiency (Hi) (return temperature 60°C)** | 98.4 % | | **Part load central heating efficiency (92/42/EEC)**  **(return temperature 30°C)** | 108.5 % | | **NOX annual emissions G20 (H-gas) (EN 15502: O2 = 0%)** | 39 Mg/kWh | | **NOMINALWATER FLOW RATE @ ΔT = 20K** | 1.82 l/s | | **MIN. NECESSARY WATER FLOW** | 0.4 m3/h | | **MIN. /MAX NOMINAL OUTPUT @ 50/30°C** | 34.6/161.5 kW | | **MIN. /MAX NOMINAL OUTPUT @ 80/60°C** | 31.5/152.9 kW | | **MIN. /MAX GAS FLOW – NAT. GAS** | 3.4-16.5 m3/hr | | **MIN. /MAX GAS FLOW – PROPANE** | 1.4 – 6.3 m3/hr | | **MIN / MAX FLUE GAS MASS FLOW RATE** | 57 / 277 kg/h | | **PRESSURE AVAILABLE AT BOILER OUTLET** | 200Pa | | **WATER CONTENT** | 17 L | | **NET WEIGHT** | 147kg | | **Triple E No. (ACA)** | Currently being processed | | **Note 1.** | Boiler to be wall hung gas condensing | | **Note 2.** | Useful efficiency at 30 % of rated heat output 97.2% GCV  according to commission regulation (EU) n° 813/23013 | | **Note 3.** | Boiler to have monoblock heating body in aluminium/silicium | | **Note 4.** | Boiler, gas premix burner in stainless steel with a surface in woven metallic fibres, modulating from 18 to 100% of output. | | **Note 5.** | Boiler fan to be fitted with air intake silencer. | | **Note 6.** | Boiler t obe supplied with MK2 or MK3 controller | | **Note 7.** | Manufacturer to be DeDietrich as supplied by Hevac Ltd., Muirfield Drive, Naas Road, Dublin 12. Tel. 01-419 1919 | |  |  | |  | | |

